## RW Comparison Worksheet Instruc
Reclaimed Water Benefit Cost Calculator for Industrial Applications - Worksheet Instructions |  |  |  |  | MODEL DISCLAIMER
1. Is reclaimed water service available to your operation? If Yes, continue to Question 2. If No, Stop Here. |  | YES, continue to Question 2. |  | NO, Stop Here | The Reclaimed Water Benefit-Cost Calculator for Industrial is to be used to provide guidance as to the economic feasibility of using reclaimed water for a specific purpose. The values that the user will input into the model are estimates and the model results should not be the only factor in determining economic feasibility. Instead, the model results should be viewed in the proper context of all other information submitted and relevant to the water use permit application or renewal.
2. Is reclaimed water the only water source available to your operation? If Yes, Stop Here. If No, continue to Question 3 and complete the RW Comparison Worksheet. |  | YES, Stop Here |  | NO, continue to Question 3 and complete the RW Comparison Worksheet.
3. What other water source(s) are available to your operation? |  | Floridan aquifer |  |  | The example values used in the models and referenced in the accompanying report are purely illustrative for the purposes of this study presentation only. Readers and users are advised to develop proper estimates of costs and benefits that would be appropriate for their individual site(s). Except where explicitly directed (e.g., to obtain the proper values of nitrogen fertilizer and fuel costs from specific websites), the example values provided in the model and in this report are NOT “default” values.
Intermediate aquifer
Surface water source
Other, please specify:
4. Of these water sources, which is the water source that would be replaced, in whole or in part, by reclaimed water? For the purposes of the RW Comparison Worksheet, this water source will be called the "Next Available Water Source" or NAWS.
5. Has the applicant obtained, from the reclaimed water provider, the nutrient contents and chemical constituents in the reclaimed water, including nitrogen, phosphorus, potassium, trace elements including boron, and the electrical conductivity and sodium absorption ratio (sodium, chloride and magnesium) of the water? This information should be used to assist in estimating the benefits and costs of using reclaimed water. |  |  | YES ______ NO _____ |  | For information regarding how to use this Reclaimed Water Benefit-Cost Calculator for Industrial Applications, please read Chapter 4.0 Industrial / Commercial Reclaimed Water Users beginning on page 4-25 found in the document titled "Economic Feasibility of Reclaimed Water Use by Non-Utility Water Use Permittees and Applicants", Final Report, June 2010, prepared by Hazen and Sawyer for the Southwest Florida Water Management District, Brooksville, Florida.
Enter the information in the Spreadsheet titled "RW Comparison Worksheet".
The other spreadsheets calculate values referred to by the "RW Comparison Worksheet" spreadsheet.
Color Code of RW Comparison Worksheet
means calculated numbers
means entered by user
means this is a drop down menu
means parameters of equations (assumed values)
means keep as blank cell
Use the following sources to determine prevailing energy costs:
Gasoline and Diesel Fuel: | U.S. Government: | http://tonto.eia.doe.gov/oog/info/gdu/gasdiesel.asp
| AAA: | http://www.fuelgaugereport.com/FLmetro.asp
Electricity: | U.S. Government: | http://www.neo.ne.gov/statshtml/115.htm
http://www.eia.doe.gov/cneaf/electricity/epm/table5_6_a.html
If needed, for fertilizer prices go to:
http://www.ers.usda.gov/Data/FertilizerUse/
Use Table 7 (Excel Spreadsheet) to determine the current price of fertilizer. Scroll down to the most recent year and use the cost of "Urea 45-46% Nitrogen.
Prepared by: Hazen and Sawyer, July 8, 2010

## RW Comparison Worksheet
Reclaimed Water Benefit-Cost Calculator for Industrial Applications
Economic Comparison of Reclaimed Water Versus Next Available Water Source For Industrial Applications
Row No. | Benefit or Cost Item | Next Available Water Source (NAWS) | Reclaimed Water Used Instead & Other Sources if Applicable (RW/Other) | NAWS Minus RW/Other (Except A. which is RW/Other minus NAWS)
(1) | (2) | (3) | (4) | (5)
1 | Name of Next Available Water Source / Name of Reclaimed Water Provider | Floridan Aquifer | Utility Name |  | MODEL CALCULATIONS
2 | A. Amount of Water Needed and Available in million gallons - Annual | 74 | 84 | 10
3 | B. Installation Costs (if not already installed or replaced) (a) |  |  |  | Annualized Installation Cost
4 | (a) The replacement cost of existing items within five years of the end of their useful lives should be included in this list as if purchased new. The remaining or "salvage" value of these existing items may be entered as indicated below. Do not forget to consider the cost of the backup water supply in Column (4) should reclaimed water be temporarily unavailable. The user may enter all appropriate names of cost items in Column (2), Rows 5 to 12. |  |  |  | Next Available Water Source Other Than Reclaimed Water | If Reclaimed Water is Used Instead
5 | Pipes and Pumps | 150000 | 200000 |  | 20380.1937 | 27173.5916
6 | Storage (minimum 5 days of capacity) - Example cost for Tank is $1.50/gal and for Lined Pond $0.40/gal of storage. | 405479.4521 | 460273.9726 |  | 35351.5464 | 40128.7824
7 | Treatment system - Example cost for Gravity filters is $400/square foot and pressure filters is $1000/square foot. | 8000 | 16000 |  | 1433.0801 | 2866.1603
8 | Land Development not included in items above | 4000 | 5000 |  | 348.7382 | 435.9228
9 | Item 1: Permitting Costs | 0 | 0 |  | 0 | 0
10 | Item 2: | 6000 | 4000 |  | 815.2077 | 543.4718
11 | Item 3: | 7000 | 8000 |  | 951.0757 | 1086.9437
12 | Item 4: | 8000 | 9000 |  | 1086.9437 | 1222.8116
13 | Salvage Value of Existing Items that are replaced and included above (enter value as a negative number). It is included as 1/5th of this value in Total Annualized Installation Cost below. | -20000 | 0
14 | Total Installation Cost | 568479.4521 | 702273.9726
15 | Annual Interest Rate (i.e. 6%) | 6% | 6% |  | Color Code
16 | Useful Life of Items in Years |  |  |  |  | means calculated numbers
17 | Pipes and Pumps | 10 | 10 |  |  | means entered by respondent
18 | Storage (minimum 5 days of capacity) - Example cost for Tank is $1.50/gal and for Lined Pond $0.40/gal of storage. | 20 | 20 |  |  | means this is a drop down menu
19 | Treatment system - Example cost for Gravity filters is $400/square foot and pressure filters is $1000/square foot. | 7 | 7 |  |  | means parameters of equations (assumed values)
20 | Land Development not included in items above | 20 | 20 |  |  | means keep as blank cell
21 | Item 1: Permitting Costs | 10 | 10
22 | Item 2: | 10 | 10 |  | Use the following sources to determine prevailing energy costs:
23 | Item 3: | 10 | 10 |  | Gasoline and Diesel Fuel: | U.S. Government: | http://tonto.eia.doe.gov/oog/info/gdu/gasdiesel.asp
24 | Item 4: | 10 | 10 |  |  | AAA: | http://www.fuelgaugereport.com/FLmetro.asp
25 | Total Annualized Installation Cost | 56366.7856 | 73457.6842 | -17090.8986 | Electricity: | U.S. Government: | http://www.neo.ne.gov/statshtml/115.htm
26 | Total Annualized Installation Cost per 1,000 Gallons of Water | 0.76171 | 0.8745 | -0.20346 |  |  | http://www.eia.doe.gov/cneaf/electricity/epm/table5_6_a.html
27 | C. Annual O&M Costs
28 | 1.0 Payments to Utility Company and, if applicable, to NAWS water utility
29 |  | 5000 | 3000
30 | Price per 1,000 gallons | 0.45 | 0.15
31 | Total Utility Payment - Annual | 38300 | 15600 | 22700
32 | 2.0 Pumping Energy Cost - Annual
33 | Energy Source: | Electricity | Electricity
34 | Total Dynamic Head in Feet: | 30 | 30
35
36 | Cost of energy source, Dollars per KWH or gallon (obtain from appropriate web site): | 0.1142 | 0.1142 |  | Next Available Water Source Other Than Reclaimed Water
37 | Energy cost to pump 1 Kgal: | 0.016309 | 0.016309 | 0 | Calculate energy cost to pump 1,000 gallons of water, depending upon fuel source per 1,000 gallons.
38 | Total pumping energy cost - Annual | 1206.8916 | 1369.9851 | -163.0935 | Electricity | 0.016309 | 0.14281 | KWH required to pump 1,000 gallons
39 | 3.0 Water System Maintenance Labor Cost - Annual |  |  |  | Diesel | N/A | 0.011425 | gallons diesel fuel required to pump 1,000 gallons
40 | Labor Cost per Hour: | 10 | 10 |  | Gasoline | N/A | 0.014913 | gallons gasoline required to pump 1,000 gallons
41 | Pumping System Labor Hours: | 52 | 26 |  | Unit Cost: | 0.016309
42 | Water System Labor Hours | 156 | 208
43 | Water Treatment Labor Hours: | 0 | 52
44 | Total Maintenance Labor Cost - Annual | 2080 | 2860 | -780
45 | 4.0 Annual Cost of Treatment Chemicals, specify chemical name |  |  |  | Reclaimed Water
46 | Chemical Name: Biocide | 0 | 5000 | -5000 | Calculate energy cost to pump 1,000 gallons of water, depending upon fuel source per 1,000 gallons.
47 | Chemical Name: | 0 | 0 | 0 | Electricity | 0.016309 | 0.14281 | KWH required to pump 1,000 gallons
48 | Chemical Name: | 0 | 0 | 0 | Diesel | N/A | 0.011425 | gallons diesel fuel required to pump 1,000 gallons
49 | 5.0 Reporting or Record Keeping Costs - Annual | 500 | 1500 | -1000 | Gasoline | N/A | 0.014913 | gallons gasoline required to pump 1,000 gallons
50 | 6.0 Other Annual Costs, specify below |  |  |  | Unit Cost: | 0.016309
51 | Item A: Residual waste disposal | 5000 | 10000 | -5000
52 | Item B: | 0 | 0 | 0
53 | Item C | 0 | 0 | 0
54 | Total Annual O&M Cost | 47086.8916 | 36329.9851 | 10756.9065
55 | Total Annual O&M Cost per 1,000 Gallons of Water | 0.63631 | 0.4325 | 0.12806 | Annualized Recurring O&M Costs
56 | D. Recurring O&M Costs, Other than Annual |  |  |  | Next Available Water Source Other Than Reclaimed Water | If Reclaimed Water is Used Instead
57 | Filter Media Replacement | 11000 | 11000 |  | 2611.3604 | 4115.2079
58 | Item a replaced: | 0 | 0 |  | 0 | 0
59 | Item b replaced: | 500 | 3000 |  | 187.0549 | 712.1892
60 | Item c replaced: | 400 | 2000 |  | 149.6439 | 474.7928
61 | Item d replaced: | 300 | 1000 |  | 112.2329 | 237.3964
62 | Replacement Frequency - No. of Years
63 | Filter Media Replacement | 5 | 3
64 | Item a replaced: | 5 | 3
65 | Item b replaced: | 3 | 5
66 | Item c replaced: | 3 | 5
67 | Item d replaced: | 3 | 5
68 | Total Annualized Recurring O&M Cost | 3060.2922 | 5539.5863 | -2479.2942
69 | Total Annualized O&M Cost per 1,000 Gallons of Water | 0.67766 | 0.49845 | -0.029515
70 | Total Annualized Cost (Negative cost means cost increase associated with reclaimed water) | 106513.9694 | 115327.2557 | -8813.2862
71 | Total Annualized Cost Per 1,000 Gallons of Water (Negative cost means cost increase associated with reclaimed water) | 1.4394 | 1.3729 | -0.10492
72 | E. Value of Additional Water Available from Reclaimed Water Source
73 | Additional Water Available from Reclaimed Water Source in million gallons per year compared to amount needed and available from NAWS- Annual: |  |  | 10
74 | What is the cost per 1,000 gallons to obtain this fresh water, including any pumping costs? This is a lower bound estimate of the value of water to the operation. The actual value is likely much higher than this value. (This can be calculated by the user using another spreadsheet.) |  |  | 0.45
75 | Value of Additional Water Available from Reclaimed Water Source - Annual |  |  | 4500
76 | F. Value of the Additional Water "Freed Up" by the Reclaimed Water Use
77 | Percent of water needed and available from NAWS that will be "freed up" and used for other purposes when reclaimed water used (% of water amount entered in Row 2, Column (3)): |  |  | 20%
78 | Amount of fresh water that would be "freed up" due to the reclaimed water use and would be used for other reasonable / beneficial uses by the applicant during a year in million gallons (on average)? |  |  | 14.8
79 | Cost per 1,000 gallons of fresh water, including any pumping costs. This is a lower bound estimate of the value of water to the operation. The actual value is likely much higher than this value. (From E. above) |  |  | 0.45
80 | Value of "freed up" NAWS water - Annual |  |  | 6660
81 | G. Value of Water Available During NAWS Water Shortage Restrictions
82 | Number of years every ten years when NAWS Water Shortage Restriction in Place |  |  | 1
83 | Percent of total annual water use that is used during the months when NAWS Water Shortage Restriction in Place |  |  | 30%
84 | Cutback percent or percent of NAWS water use that is cut back during water restriction period: |  |  | 20%
85 | Annualized amount of water available during NAWS Water Shortage Restriction Due to Reclaimed Water Use in million gallons per year |  |  | 0.444
86 | Cost per 1,000 gallons of fresh water, including any pumping costs. This is a lower bound estimate of the value of water to the operation. The actual value is likely much higher than this value. (From I. below) |  |  | 0.45
87 | Value of Water Available During NAWS Water Shortage Restrictions |  |  | 199.8
88 | Total Benefit Value of Reclaimed Water (Other Than Cost Savings) - Annual |  |  | 11359.8
89 | Total Benefit Value of Reclaimed Water per 1,000 Gallons of Reclaimed Water (Other Than Cost Savings) |  |  | 0.13524
90 | Net Benefit of Reclaimed Water Use Relative to Next Available Water Source - Annual (b) |  |  | 2546.5138
91 | Net Benefit of Reclaimed Water Use Relative to Next Available Water Source Per 1,000 Gallons of Reclaimed Water (b) |  |  | 0.030316
92 | (d) Net Benefit is the sum of the benefits minus the sum of the costs of RW/Other. These are benefits and costs when compared to the Next Available Water Source (NAWS). A positive number means the estimated value of the total benefit of RW/Other is greater than the estimated value of the total cost of RW/Other. A negative number means the estimated value of the total benefit of RW/Other is less than the estimated value of the total cost of RW/Other.
Note on E30: gjohns: The cost per 1,000 gallons of water was calculated using 74.00 mg for NAWS and using 84.00 mg for reclaimed water and for NAWS Minus RW. This is why Column (5) is not equal to Column (3) minus Column (4) in Row 26).
Note on B43: gjohns: For RW/Other, when considering the backup water system that would be needed in the event that reclaimed water is temporarily unavailable, the user should include only those labor hours associated with maintaining the backup system so that it will operate when needed, in addition to any other relevant costs not associated with the backup system.
Note on B50: gjohns: The user may enter the name of a different cost item here.
Note on E59: gjohns: The cost per 1,000 gallons of water was calculated using 74.00 mg for NAWS and using 84.00 mg for reclaimed water and for NAWS Minus RW. This is why Column (5) is not equal to Column (3) minus Column (4) in Row 55).
Note on B61: gjohns: The user may enter the name of a different cost item here.
Note on E73: gjohns: The cost per 1,000 gallons of water was calculated using 74.00 mg for NAWS and using 84.00 mg for reclaimed water and for NAWS Minus RW. This is why Column (5) is not equal to Column (3) minus Column (4) in Row 69).
Note on E75: gjohns: The cost per 1,000 gallons of water was calculated using 74.00 mg for NAWS and using 84.00 mg for reclaimed water and for NAWS Minus RW. This is why Column (5) is not equal to Column (3) minus Column (4) in Row 71).

## Next Available Source Pump Ener
Pumping Energy Equations - Next Available Water Source
Electicity | Matches EEE paper | Matches SWFWMD calcs | Matches Jorge paper
Total Dynamic Head (TDH) in feet | 300 | 30 | 245
Gallons per Minute of flow (GPM) | 1000 | 200 | 25
Pump efficiency | 0.75 | 0.75 | 0.64 | Gal of diesel fuel used per hour of pumping, 1000 gpm, 300 tdh | kWh of electricity | Gallons per hour of gasoline
Motor power in hp (brake horsepower) | 101.1122 | 2.0222 | 2.4192 | 6.8551 | 84.9683 | 8.948 | From EEE Paper
hp-hours per gallon | 1.18 | 1.18 | 1.127 | 0.95763
One hour or Hours it takes to pump 1,000 gallons | 1 | 0.083333 | 6 | 1.1265 | 1.341 |  |  | 11.0011
kWh of electicity needed | 85.6883 | 0.14281 | 12.8794 | 12.875 | 0.88 | 1.1801 |  | 0.89
Cost per kWh | 0.119 | 0.1142 | 0.119 |  | 1.1265 |  |  | 1.1871 | 14.6628
Cost of electricity per 1,000 gallons | 10.1969 | 0.016309 | 1.5327
Motor efficiency assumed to be 0.88. |  |  |  | From IFAS "Loading Effects on Irrigation Power Unit Performance, A.G. Smajstrla nad F.S. Zazueta, AE 242, June 2003.
| 7.1407 |  |  | From Energy Efficiency & Environmental News: Energy Use in Irrigation, Nov. 1991, Florida Energy Extension Service and Helen H. Whiffen.
5
Diesel fuel | Matches EEE paper
Total Dynamic Head (TDH) in feet | 300 | 30
Gallons per Minute of flow (GPM) | 1000 | 200
Pump efficiency | 0.75 | 0.75
Motor power in hp | 101.1122 | 2.0222 | From Hydraulic Machines and Equipment, page 18-7, Professional Publications Inc. (Jorge Atoche) and Energy Efficiency and Environmental News: Energy Use in Irrigation, IFAS.
hp-hours per gallon | 14.75 | 14.75 | From IFAS Energy Requirement for Drip Irrigation of Tomatoes in North Florida and Loading Effects on Irrigation Power Unit Performance, BUL 289, July 2002.
One hour or Hours it takes to pump 1,000 gallons | 1 | 0.083333
Gallons of diesel fuel needed | 6.8551 | 0.011425 | 0.57126 | 0.067797
Cost per Gallon of diesel fuel | 2.772 | 0.1142 | See sources in Pumping Costs SS
Cost of diesel fuel per 1,000 gallons | 19.0022 | 0.0013047
Motor efficiency assumed to be 0.88.
Gasoline | Matches EEE paper | Answer
Total Dynamic Head (TDH) in feet | 300 | 30
Gallons per Minute of flow (GPM) | 1000 | 200
Pump efficiency | 0.75 | 0.75
Motor power in hp | 101.1122 | 2.0222
hp-hours per gallon | 11.3 | 11.3
One hour or Hours it takes to pump 1,000 gallons | 1 | 0.083333
Gallons of gasoline fuel needed | 8.948 | 0.014913
Cost per Gallon of gasoline fuel | 2.626 | 0.1142
Cost of gasoline fuel per 1,000 gallons | 23.4974 | 0.0017031
Motor efficiency assumed to be 0.88.
Note on C4: gjohns: The gpm cancels out of equation in cell C9. It doesn't matter what number you put here.
Note on C18: gjohns: The gpm cancels out of equation in cell C23. It doesn't matter what number you put here.
Note on C30: gjohns: The gpm cancels out of equation in cell C35. It doesn't matter what number you put here.

## Reclaimed Water Pump Energy
Pumping Energy Equations - Reclaimed Water
Electicity | Matches EEE paper | Matches SWFWMD calcs | Matches Jorge paper
Total Dynamic Head (TDH) in feet | 300 | 30 | 245
Gallons per Minute of flow (GPM) | 1000 | 200 | 25
Pump efficiency | 0.75 | 0.75 | 0.64 | Gal of diesel fuel used per hour of pumping, 1000 gpm, 300 tdh | kWh of electricity | Gallons per hour of gasoline
Motor power in hp (brake horsepower) | 101.1122 | 2.0222 | 2.4192 | 6.8551 | 84.9683 | 8.948 | From EEE Paper
hp-hours per gallon | 1.18 | 1.18 | 1.127 | 0.95763
One hour or Hours it takes to pump 1,000 gallons | 1 | 0.083333 | 6 | 1.1265 | 1.341
kWh of electicity needed | 85.6883 | 0.14281 | 12.8794 | 12.875 | 0.88 | 1.1801
Cost per kWh | 0.119 | 0.1142 | 0.119 |  | 1.1265
Cost of electricity per 1,000 gallons | 10.1969 | 0.016309 | 1.5327
Motor efficiency assumed to be 0.88.
Diesel fuel | Matches EEE paper
Total Dynamic Head (TDH) in feet | 300 | 30 |  | 6000
Gallons per Minute of flow (GPM) | 1000 | 200
Pump efficiency | 0.75 | 0.75
Motor power in hp | 101.1122 | 2.0222 | From Hydraulic Machines and Equipment, page 18-7, Professional Publications Inc. (Jorge Atoche) and Energy Efficiency and Environmental News: Energy Use in Irrigation, IFAS.
hp-hours per gallon | 14.75 | 14.75 | From IFAS Energy Requirement for Drip Irrigation of Tomatoes in North Florida and Loading Effects on Irrigation Power Unit Performance.
One hour or Hours it takes to pump 1,000 gallons | 1 | 0.083333
Gallons of diesel fuel needed | 6.8551 | 0.011425 | 0.57126 | 0.067797
Cost per Gallon of diesel fuel | 2.772 | 0.1142 | See sources in Pumping Costs SS
Cost of diesel fuel per 1,000 gallons | 19.0022 | 0.0013047
Motor efficiency assumed to be 0.88.
Gasoline | Matches EEE paper | Answer
Total Dynamic Head (TDH) in feet | 300 | 30
Gallons per Minute of flow (GPM) | 1000 | 200
Pump efficiency | 0.75 | 0.75
Motor power in hp | 101.1122 | 2.0222
hp-hours per gallon | 11.3 | 11.3
One hour or Hours it takes to pump 1,000 gallons | 1 | 0.083333
Gallons of gasoline fuel needed | 8.948 | 0.014913
Cost per Gallon of gasoline fuel | 2.626 | 0.1142
Cost of gasoline fuel per 1,000 gallons | 23.4974 | 0.0017031
Motor efficiency assumed to be 0.88.
Note on C4: gjohns: The gpm cancels out of equation in cell C9. It doesn't matter what number you put here.
Note on C18: gjohns: The gpm cancels out of equation in cell C23. It doesn't matter what number you put here.
Note on C30: gjohns: The gpm cancels out of equation in cell C35. It doesn't matter what number you put here.